{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["金属结构及机电设备"],"not_rendered":{"external_links":1,"defined_names":2},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"金属结构及机电设备","index":0,"n_rows":161,"n_cols":7,"rows_kept":161,"merged":[[0,0,0,1],[1,0,1,6],[154,1,154,2],[155,0,155,6],[156,0,156,5],[157,0,157,5],[158,0,158,5],[159,0,159,5],[160,0,160,5]],"flags":["formulas_cached_only"]}
["附件"]
["广东省惠州市中心城区防洪排涝综合治理工程（惠城区排涝站改造项目-老指挥部排涝站改造工程）金属结构及机电设备采购项目询价报价表"]
["序号","材料名称","规格型号或指标、技术参数","单位","数量","报价（元）","备注"]
["一","水泵机组及技术供水"]
["一）","新站水泵机电设备"]
[1,"单基础整体式轴流泵（自重6.5吨）","型号1000ZLDB-5.5，设计流量3.3m3/s，设计扬程5.5m，最高扬程7.4m，额定转速490r/min，叶片五轴联动数控加工，G1Cr18Ni9Ti材质，整体出厂吊装，水导轴承PLYhRBR或Composite(Gm2401)轴承","台",2]
[2,"双法兰传力接头","型号VSSJAF，DN1000，1.0mpa","个",2]
[3,"异步电动机(自重6.5吨)","YL450-12/280kw，280kW，380V，490r/min，F级，IP23，配套SKF轴承","台",2]
["二）","新站水泵技术给水系统"]
[1,"软密封闸阀(常开)","Z45X-10，DN50，1.0mPa","个",1]
[2,"二位二通自保持球阀","ZBF22Q-50，DN50，1.0mPa，DC24V","个",1]
[3,"软密封闸阀(常闭)","Z45X-10，DN50，1.0mPa","个",1]
[4,"仪表阀","J19F-10，DN15.1.0mPa","个",2]
[5,"压力变送器","B0803，0-0.5mPa，4-20m两线制","个",1]
[6,"压力表","Y-100，测量范围0-0.5mpa","个",1]
[7,"软密封闸阀(常开)","Z45X-10，DN25，1.0mPa","个",4]
[8,"二位二通自保持球阀","ZBF22Q-25，DN25，1.0mPa，DC24V","个",2]
[9,"热导式流量开关","型号FCS(T)，DC24V，1个常开触点","个",2]
[10,"镀锌钢管","DN50，壁厚4mm","m",25]
[11,"镀锌钢管","DN25，壁厚3.25mm","m",40]
["三）","旧站水泵设备更换"]
[1,"更换旧站小泵组(自重2t)","单基础立式轴流泵350ZLBD-100，设计流量0.25m'/s，扬程2.35~6.7m，叶片角度-2，含配套高效率三相电机22kW，泵长度6.5m","台",2]
[2,"更换旧站低压无功补偿柜","补偿容量180kvar，800x800x2260m","套",1]
[3,"更换旧站小泵起动柜","软启动器30kW，800x800x1800m","套",2]
[4,"移动式潜污泵","WQ100-10-7.5，流量100㎡/h，扬程10m，功率7.5kW","台",1]
["二","金属结构设备"]
["一）","清污及起重设备"]
[1,"抓斗除污机","型式：液压耙斗钢丝绳卷扬式：安全工作负荷：11000kg；抓斗宽度：2.5m；提升电机功率：5.5kw：提升速度10m/min；行走电机功率：2X0.75kW：行走速度：20m/min；液压泵功率：1.5kw：液压泵工作压力12mpa，轨道32a工字钢，长度18m。带PLC控制箱(留100m以太网通讯口)。","台",1]
[2,"KX4抓斗清污机控制箱","380/220V，控制1台启闭机7.5kW，304不锈钢外壳，挂墙安装","个",1]
[3,"手推小车","储渣容积≥1.5m3，不锈钢304材质","个",1]
[4,"电动单梁起重机","LX-12t，起重量12吨，跨度5.0m，起升高度18m，起升速度8/0.8m/min，行走速度20m/min，工作级别A3，地面操作，I56a工字钢轨道，长度2×16m","台",1]
[5,"KX7泵房起重机现场开关箱","380/220V，304不锈钢外壳，户内挂墙安装","个",1]
[6,"检修闸门电动葫芦","mD-10t，起升高度12m，起升速度8/0.8m/min，行走速度20m/min，工作级别A3，地面操作","台",1]
[7,"KX8检修闸门电动葫芦开关箱","380/220V，304不锈钢外壳，户内挂墙安装"]
[8,"泵站防洪闸门双吊点卷扬式启闭机(自重2.5t)","型号QPQ-2x10t，额定起重量2x10t，集中驱动方式，起升高度16m，吊点距见闸门结构图，起升速度2.3m/min，电动机功率11kW，卷筒直径400mn","台",2]
[9,"KX1~KX2防洪闸门启闭机控制箱","380/220V，控制1台启闭机7.5kW，304不锈钢外壳，挂墙安装","个",2]
[10,"自排闸闸门双吊点卷扬式启闭机(自重3t)","型号QPQ-2x16t，额定起重量2x16t，集中驱动方式，起升高度16m，吊点距见闸门结构图，起升速度2.26m/min，电动机功率13kW，卷简直径400mmn","台",1]
[11,"KX3自排闸门启闭机控制箱","380/220V，控制1台启闭机11kW，304不锈钢外壳，挂墙安装","个",1]
[12,"电动葫芦轨道","40a工字钢，不含埋件","m",20]
["二）","闸门、拦污山、拍门设备"]
[1,"水闸防洪闸闸门7×5（1扇）","含防腐。钢表面采用喷砂(或抛丸)除锈，清除铁锈污物基体金属的表面清洁度等级不低于Sa2.5级。表面涂环氧富锌底漆一道不低于60μm，环氧云铁中间漆二道，每道80μm，最后涂氣化橡胶面漆一道80μm。","t",13.12]
[2,"闸门预埋件（1套）","含防腐。钢表面采用喷砂(或抛丸)除锈，清除铁锈污物基体金属的表面清洁度等级不低于Sa2.5级。表面涂环氧富锌底漆一道不低于60μm，环氧云铁中间漆二道，每道80μm，最后涂氣化橡胶面漆一道80μm。","t",3.74]
[3,"排涝站检修闸门3.44×4（1扇）","含防腐。钢表面采用喷砂(或抛丸)除锈，清除铁锈污物基体金属的表面清洁度等级不低于Sa2.5级。表面涂环氧富锌底漆一道不低于60μm，环氧云铁中间漆二道，每道80μm，最后涂氣化橡胶面漆一道80μm。","t",5.25]
[4,"闸门预埋件（2套）","含防腐。钢表面采用喷砂(或抛丸)除锈，清除铁锈污物基体金属的表面清洁度等级不低于Sa2.5级。表面涂环氧富锌底漆一道不低于60μm，环氧云铁中间漆二道，每道80μm，最后涂氣化橡胶面漆一道80μm。","t",{"v":8.374,"d":"8.37"}]
[5,"排涝站防洪闸门3.3×5（2扇）","含防腐。钢表面采用喷砂(或抛丸)除锈，清除铁锈污物基体金属的表面清洁度等级不低于Sa2.5级。表面涂环氧富锌底漆一道不低于60μm，环氧云铁中间漆二道，每道80μm，最后涂氣化橡胶面漆一道80μm。","t",{"v":12.718,"d":"12.72"}]
[6,"闸门预埋件（2套）","含防腐。钢表面采用喷砂(或抛丸)除锈，清除铁锈污物基体金属的表面清洁度等级不低于Sa2.5级。表面涂环氧富锌底漆一道不低于60μm，环氧云铁中间漆二道，每道80μm，最后涂氣化橡胶面漆一道80μm。","t",{"v":7.065,"d":"7.07"}]
[7,"老站拦污栅栅体（第一道）","组件及埋件均涂防锈漆及灰色环氧磁漆两遍。","t",{"v":6.833,"d":"6.83"}]
[8,"老站拦污栅预埋件（第一道）","组件及埋件均涂防锈漆及灰色环氧磁漆两遍。","t",{"v":2.313,"d":"2.31"}]
[9,"排涝站拦污栅栅体","组件及埋件均涂防锈漆及灰色环氧磁漆两遍。","t",{"v":4.127,"d":"4.13"}]
[10,"排涝站拦污栅预埋件","组件及埋件均涂防锈漆及灰色环氧磁漆两遍。","t",2.68]
[11,"节能型不锈钢自由侧翻式拍门（配缓冲装置）","孔口直径Φ1500mm，圆形单门，最大工作水头10.0m，阻力系数≤0.1，开启角度80°以上，水头损失≤0.04m，开启力(非淹没)小于门重1/5，带缓冲装置","套",{"v":2,"d":"2.00"}]
["三","电气、自动化、监测设备"]
["一）","高低压配电设备"]
[1,"Tm1主变压器","SCB18-800/10，800KVA(全铜绕组带不锈钢外壳)","台",1]
[2,"Tm2站用变压器","SCB18-100/10，100KVA(全铜绕组带不锈钢外壳)","台",1]
[3,"G01.G0610KV高压进线柜","KYN28A-12(800x1500x2260mm)含微机保护装置","面",2]
[4,"G02.GO51OKV高压计量柜","KYN28A-12(800x1500x2260mm)","面",2]
[5,"G03~G0410KV变压器出线柜","KYN28A-12(800x1500x2260mm)含微机保护装置","面",2]
[6,"PO1Tm1低压考核柜","GCK(800x800x2260mmm)","面",1]
[7,"P02Tm1低压受电柜","GCK(800x800x2260mm)","面",1]
[8,"P03Tm1电容补偿柜","GCK(800x800x2260mm)","面",1]
[9,"P041#低压移磁无级调压启动装置","RYZQ-D-280KW/380V(800x800x2260mm","面",1]
[10,"P052#低压移磁无级调压启动装置","RYZQ-D-280KW/380V(800x800x2260mm","面",1]
[11,"ZL直流电源屏","直流系统65AH/220V；高频开关采用N+1冗余配置；18节12V蓄电池；蓄电池使用寿命：10年及以上（25℃）；2面屏柜（800*600*2260）；电池采用汤浅、阳光或荷贝克","套",1]
[12,"PO6Tm2低压考核柜","GCK(800x800x2260mm","面",1]
[13,"P07Tm2双电源转换柜","GCK(800x800x2260mm","面",1]
[14,"P08Tm2电容补偿柜","GCK(800x800x2260mm","面",1]
[15,"PO9.P10Tm2低压出线柜","GCK(800x800x2260mm","面",2]
[16,"静音型柴油发电机组","80kW.O.4KV.柴油发电机组、静音外壳、控制箱。蓄电池。消声器防震胶、排风槽、排风百叶密及必需附件等、带自启动功能。","台",1]
[17,"电力电缆","YJV-8.7/15kV-3x70","m",27]
[18,"电力电缆","YJV-1kV-3x185+1x95","m",100]
[19,"电力电缆","YJV-1kV-4x70+1x35","m",52]
[20,"锚筋","Ф12，L=400mm","根",120]
[21,"钢板","150x150x8","块",60]
[22,"槽钢","10号","米",48]
[23,"集合式低压母线槽","1600A/4P，含吊架","m",6]
[24,"母线槽终端头","配套1600A/4P","个",2]
[25,"电缆头","配套YJV-8.7/15kV-3x70","套",4]
[26,"电缆头","配套YJV-1kV-3x185+1x95","套",12]
[27,"电缆头","配套YJV-1kV-4x70+1x35","套",4]
[28,"10kV电缆输电线路","双回路一线、二线分接箱接线，ZRYJV22-8.7/15kV-3x70，电缆沟转穿Ф110电缆管","m",500,null,"暂估"]
["二）","电气控制设备"]
[1,"DL1泵房动力配电箱","380/220V，304不锈钢外壳，挂墙安装","个",1]
[2,"DL2防洪水闸动力配电箱","380/220V，304不锈钢外壳，挂墙安装","个",1]
[3,"KX5电机加热器控制箱","380/220V，控制2合电机加热器2x2KW，304不锈钢外壳，挂墙安装","个",1]
[4,"KX6风机控制箱","380/220V，控制8合风机机8x0.25kW，304不锈钢外壳，挂安装","个",1]
[5,"电力电缆","YJV-1kV-4x25+1x16","m",192]
[6,"电力电缆","YJV-1kV-5x10","m",172]
[7,"电力电缆","YJV-1kV-4x10","m",141]
[8,"电力电缆","YJV-1kV-4x4","m",165]
[9,"电力电缆","YJV-1kV-3x4","m",40]
[10,"电缆头","配套YJV-1kV-4x25+1x16","套",16]
[11,"托臂","热镀锌金属托臂，b=300，含螺栓等配件","件",55]
[12,"膨胀螺栓","m12X120，含螺母、垫圈","个",122]
[13,"5mm花纹钢盖板",null,"m2",15]
[14,"电缆管","DN100镀锌钢管，δ=4mm","m",64]
[15,"电缆管","DN80镀锌钢管，δ=3.5mm","m",100]
[16,"电缆管","DN50镀锌钢管，δ=3.5mm","m",74]
[17,"电缆管","DN40镀锌钢管，δ=3mm","m",250]
[18,"电缆管","DN25镀锌钢管，δ=2.5mm","m",110]
["三）","监测及信息化设备"]
[1,"不间断电源UPS(含后备电池组)","容量：6kVA/2h，工作方式：在线式；输入：~380V；RS485通讯，主机与电池整合进柜，尺寸600X800X2260(宽x深x高)，含柜内辅材、风扇、温湿度控制器。","套",1]
[2,"UPS电源配电箱","380/220V.11出线","个",1]
[3,"网络柜","380/220V.11出线","套",1]
[4,"控制台","长×宽×高=2000×1200×750mm，防火实木板材制作","套",1]
[5,"控制台座椅","真皮，铝合金脚","张",2]
[6,"闸门开度仪","范围：0-8m，分辨率：1mm，传感器：多圈绝对型光电编码器，配套显示仪，带RS485接口","个",3]
[7,"闸门荷重仪","HZY-3型；测量范围：0~300KN；分辨率：0.01KN；精度：±0.1%F·S±0.1KN","个",3]
[8,"行程开关","LXK4-048/1(3常闭3常开)","个",6]
[9,"一杆式水位雨量视频监测站","包括：30米量程水位计1个；0.5m量程翻斗式雨量计1个：遥测终端RTU1个；遥测终端箱1个；5m监测立杆及基础1根等","套",1]
[10,"一杆式水位视频监测站","包括：30米量程水位计1个；遥测终端RTU1个；遥测终端箱1个；5m监测立杆及基础1根等","套",1]
[11,"工业级交换机","24个10/100/1000Base-T自适应电口，交换容量>336Gbps/3.36Tbps，支持全端口线速转发；支持终端识别、终端准入、安全防护；支持胖瘦一体化","台",1]
[12,"视频监控操作员站","11代i7-11700F16G1T+256GRX550X4G独显win11)23英寸","套",1]
[13,"视频监控管理服务器","R740服务器主机/2*至强银牌4210R十核2.4GHz/16G*4/4TSAS*3/H730P-2G/750W双电/导轨/三年保修","套",1]
[14,"NVR硬盘录像机(24路）","硬件规格：3U标准机架式；2个HDMI，2个VGA，HDMI+VGA组内同源；16盘位，可满配8T、10T硬盘，支持硬盘热插拔；2个千兆网口、2个USB2.0接口、1个USB3.0接口、1个eSATA接口；支持RAID0、1、5、10，支持全局热备盘","台",1]
[15,"4TB企业级硬盘","容量：4T，接口类型：SATA，接口速率：6Gb/s","个",7]
[16,"全彩筒型摄像机","400万像素，最高分辨率可2560X1440@25fps；智能侦测：支持越界侦测，区域入侵侦测；持萤石平台接入，内置麦克风，高清拾音。","套",4]
[17,"智能全彩球机","400万像素，支持区域入侵侦测、进入区域侦测和离开区域侦等智能侦测并联动跟踪；支持切换为人脸抓拍模式，采用可见光补光30m，支持超低照度。","套",12]
[18,"6米监控立杆及基础","6米，100~150锥管，壁厚3.5m，带避雷针；基础长500*宽500*深1000m(基础开挖，接地极，地笼(预埋件)，混凝土C20砼，回填)","套",3]
[19,"前端安装箱","350x350x200，IP54，SS3041.5mm厚","个",16]
[20,"电源防雷器","Uc≥AC/DC28V，Up≤1.5kV，Iimp>20KA(I类试验)","个",16]
[21,"信号防雷器","Uc>6V，155MHz，Iimp>2.5KA(I类试验)","个",16]
[22,"光纤收发器","网管型，1个百兆单模光口，2个百兆电口，卡轨式，AC220V供电","对",16]
[23,"摄像机电源","DC24V开关电源","个",16]
[24,"调度中心寻呼主机","E-A32i，配备鹅颈麦克风，功能强大。","个",1]
[25,"鹅颈播音话筒","电容式；频率响应：100Hz-16000Hz；输出阻抗：200Ω；灵敏度：-43dB±2dB；指向性：心型指向；参考拾音距离：20-50cm","个",1]
[26,"广播网关","参考型号E-PA3，远程广播网关","个",1]
[27,"扬声器","全频防水喇叭；额定功率：60W；灵敏度：93dB；频率响应：70HZ-16KHz；输入电压：70/110V；安装方式：壁挂式；IP66六级防水防尘。","个",1]
[28,"控制电缆","4芯单模光纤ZR-RVV-3x4","m",692]
[29,"控制电缆","KVVP-2×4","m",116]
[30,"控制电缆","KVVP-4×1.5","m",46]
[31,"控制电缆","KVVP-6×1.5","m",40]
[32,"控制电缆","KVVP-8×1.5","m",10]
[33,"控制电缆","ZR-RVV-3×4","m",386]
[34,"控制电缆","六类双绞线UTP-6","m",176]
[35,"电缆保护管","PVC32","m",1118]
["四）","排涝站安全监测设备"]
[1,"渗压计","型式：振弦式；量程：0.35Mpa；分辨率：0.025%FS；精度：0.1%FS","套",12]
[2,"现地控制单元(MCU)","10通道","台",2]
[3,"水工监测电缆","GK/BGK02-335VT8","m",384]
[4,"穿线管","PE32","m",240]
[5,"测压管","预埋304不锈钢管DN50(透水花管)壁厚5mm","m",144]
[6,"测压管管口钢盖板","长0.5m，宽0.5m，厚10mm","个",12]
[7,"工程安全监测专业分析评价软件","软件具有数据管理、分析、报警、图形界面展示、预测评价等功能","套",1]
["五）","排涝站安全监测设备"]
[1,"压电式加速度传感器","VS-025，灵敏度：100mV/g，频响范围：0.5Hz～14000Hz(±3dB），加速度范围：±80gpeak，温度响应：-50°C～121°C，供电电压：18～30VDC，外壳材质：不锈钢。","个",8]
[2,"电涡流摆度传感器","TS-CWY-D0，探头直径：Φ8mm，线性范围：8mm，灵敏度：8.0V/mm±4%，线性度：系统误差≤±1%，频响特性：0～10KHz，配5米电缆。","套",4]
[3,"转速传感器","RS-02，测量范围：0～20000个脉冲/秒，测量精度：±1个脉冲/秒，安装距离：0.5～4mm，响应频率：1Hz～20KHz，输出方式：PNP开路输出。","个",2]
[4,"压力变送器","测量范围：-0.1～0.1MPa，测量精度：≤±0.15%FS，配5米电缆。","个",2]
[5,"就地接线箱","提供40个端子","台",2]
[6,"数据采集单元","1路通道，RS-485通讯口","台",14]
[7,"压力显示仪","压力变送器配套","台",2]
[8,"在线状态监测装置","输入信号：振动、摆度、转速、压力等传感器，12通道，10.2英寸真彩色触摸屏显示，测量精度：%%P0．5级，线性误差≤1%FS（满量程），以太网接口","台",2]
[9,"机组在线监测箱","每台机组设1个在线监测箱，材质：304不锈钢","套",2]
[null,"总合计"]
["注：1、单价包含材料费（包含配套材料、辅助材料等）、人工费、机械费、制作安装费、试验检测费、包装费、运杂费（包括装卸车费）、培训费、保险费、缺陷修复费、综合管理费、技术资料费、风险费、利润、税费（13%）、政策性文件规定费用等一切费用，即货物到达交货地点所发生的一切费用；数量以采购人实际采购数量为准，经验收合格后按送货量月结80%（进度款到账的情况下），当年结算至实际供货量的97%，实际供货款的3%作为质保金，质保金待完工一年后付清，具体以签订的合同条款为准。\n2、以上清单项目特征以施工图纸及答疑回复为准。（邹工：13480512816）"]
["供应商名称："]
["供应商地址："]
["联系人："]
["联系电话："]
["日期："]